# SPRINGER-NATURE APPLIED SCIENCES

# SUPPLEMENTARY DATA

# System-Wide Joint-Dynamic-Response Approach to Water Quality Evaluation in Distribution Networks with Multiple Service Reservoirs and Pumps

Tiku T. Tanyimboha,* and Alemtsehay G. Seyoumb

a School of Civil and Environmental Engineering, University of the Witwatersrand, Johannesburg, Private Bag 3, WITS 2050, South Africa

b SWS Consultancy, Addis Ababa, Ethiopia

Authors

- Tiku T. Tanyimboh, PhD (*Corresponding author)

School of Civil and Environmental Engineering

University of the Witwatersrand, Johannesburg

Private Bag 3, WITS 2050, South Africa

Email: tiku.tanyimboh@wits.ac.za

Phone: +27 (0) 11 717 7105

ORCID ID: https://orcid.org/0000-0003-3741-7689

* Corresponding author

- Alemtsehay G. Seyoum, PhD

SWS Consultancy, P.O. Box 11351

Addis Ababa, Ethiopia

Email: alemgm2002@yahoo.com

Phone: +251-116-478838

# System-Wide Joint-Dynamic-Response Approach to Water Quality Evaluation in Distribution Networks with Multiple Service Reservoirs and Pumps

# SUPPLEMENTARY DATA

Table A1 Nodal demands and daily demand pattern

| Nodes | Elevations (m) | Demands (L/s) | Nodes | Elevations (m) | Demands (L/s) | Time of day | Average-day demand factor |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 6.096 | 31.54510 | 11 | 36.58 | 25.23608 | 00:00-03:00 | 0.7 |
| 2 | 15.24 | 12.61804 | 12 | 15.24 | 31.54510 | 03:00-06:00 | 0.6 |
| 3 | 15.24 | 12.61804 | 13 | 15.24 | 31.54510 | 06:00-09:00 | 1.2 |
| 4 | 24.38 | 37.85412 | 14 | 15.24 | 31.54510 | 09:00-12:00 | 1.3 |
| 5 | 24.38 | 37.85412 | 15 | 15.24 | 31.54510 | 12:00-15:00 | 1.2 |
| 6 | 24.38 | 37.85412 | 16 | 36.58 | 25.23608 | 15:00-18:00 | 1.1 |
| 7 | 24.38 | 37.85412 | 17 | 36.58 | 63.09020 | 18:00-21:00 | 1.0 |
| 8 | 24.38 | 25.23608 | 18 | 15.24 | 31.54510 | 21:00-24:00 | 0.9 |
| 9 | 36.58 | 25.23608 | 19 | 15.24 | 63.09020 |  |  |
| 10 | 36.58 | 25.23608 |  |  |  |  |  |

Table A2 Cost breakdown for selected optimal solutions of the Anytown network

|  | Cost components ($106) |  |  |  | Total deficit in residual heads (m) |
| --- | --- | --- | --- | --- | --- |
| Solutions | Pipes | Energy | Tanks | Total |  |
| Vamvakeridou-Lyroudia et al. (2005)a | 3.78 | 6.15 | 0.61 | 10.54 | 1.46 |
| Murphy et al. (1994) | 4.51 | 5.97 | 0.86 | 11.34 | 0.00 |
| Walters et al. (1999) | 4.26 | 6.04 | 0.74 | 11.04 | 0.00 |
| Walters et al. (1999) | 4.10 | 5.90 | 0.90 | 10.90 | 0.00 |
| Vamvakeridou-Lyroudia et al. (2005) | 3.89 | 6.15 | 0.61 | 10.63 | 0.00 |
| Prasad (2010) | 3.58 | 6.24 | 0.78 | 10.59 | 0.00 |
| Solution 2 (Siew et al. 2016) | 3.68 | 6.22 | 0.51 | 10.41 | 0.00 |
| Solution 1 (Siew et al. 2016) | 3.68 | 6.12 | 0.51 | 10.31 | 0.00 |
| aThis solution is infeasible due to residual head deficits of 0.78 m at node 5 and 0.68 m at node 11. |  |  |  |  |  |

Table A3 Properties of the new tanks of the solutions investigated

| Properties | Siew et al. (2016) |  | Prasad (2010) |  | Walters et al. (1999) |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Solution 1 | Solution 2 | Tank 150N | Tank 170N | Tank 5N | Tank 12N |
| Maximum operating water level (m) | 72.98 | 72.98 | 74.34 | 72.02 | aU | U |
| Minimum operating water level (m) | 67.18 | 66.56 | 69.93 | 67.33 | U | U |
| Top level (m) | 74.31 | 74.31 | 75.56 | 72.93 | U | U |
| Elevation (m) | 60.96 | 60.96 | 63.40 | 63.70 | 51.51 | 72.24 |
| Diameter (m) | 18.67 | 18.67 | 14.51 | 12.06 | U | U |
| Tank location node | 7 | 6 | 16 | 9 | 5 | 12 |
| Emergency storage fraction | 0.45 | 0.5 | U | U | 0.57 | 0.29 |
| aU denotes unavailable or unclear |  |  |  |  |  |  |

Table A4 Details of the new and rehabilitated pipes of the solutions investigated

|  | Solution 1 |  | Solution 2 |  | Prasad (2010) |  | Walters et al. (1999) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Pipe ID | Diameter (m) | Pipe ID | Diameter (m) | Pipe ID | Diameter (m) | Pipe ID | Diameter (m) | Pipe ID | Diameter (m) |
| Parallel pipes | 1 | 0.3556 | 2 | 0.6096 | 2 | 0.3556 | 1 | 0.7620 | 26 | 0.5080 |
|  | 2 | 0.6096 | 14 | 0.2032 | 20 | 0.4572 | 2 | 0.6096 | 33 | 0.2032 |
|  | 20 | 0.4064 | 17 | 0.2032 | 24 | 0.2540 | 20 | 0.5080 | 36 | 0.3048 |
|  | 23 | 0.3556 | 20 | 0.6096 | 26 | 0.5080 | 21 | 0.3048 | 39 | 0.2540 |
|  | 26 | 0.6096 | 26 | 0.6096 | 40 | 0.1524 | 23 | 0.4064 | 40 | 0.4572 |
| Pipe cleaning/ lining | 40 | 0.3048 | 3 | 0.4064 | 40 | 0.3048 | 3 | 0.4064 | 27 | 0.2032 |
| New pipes | 10 | 0.3556 | 10 | 0.1524 | 10 | 0.3048 | 10 | 0.3048 |  |  |
|  | 13 | 0.1524 | 13 | 0.2540 | 13 | 0.1524 | 13 | 0.2540 |  |  |
|  | 14 | 0.1524 | 14 | 0.2032 | 14 | 0.2032 | 14 | 0.2032 |  |  |
|  | 15 | 0.2540 | 15 | 0.4572 | 15 | 0.2540 | 15 | 0.1524 |  |  |
|  | 16 | 0.3556 | 16 | 0.2032 | 16 | 0.3048 | 16 | 0.3556 |  |  |
|  | 25 | 0.1524 | 25 | 0.2032 | 25 | 0.1524 | 25 | 0.1524 |  |  |
|  | Riser 7a | 0.4064 | Riser 6 | 0.3048 | Riser 9 | 0.2035 | Riser 5 | 0.4572 |  |  |
|  |  |  |  |  | Riser 16 | 0.3556 | Riser 12 | 0.2540 |  |  |
| aRisers 5, 6, 7, 9, 12 and 16 are the pipes that connect the new tanks to nodes 5, 6, 7, 9, 12 and 16, respectively. |  |  |  |  |  |  |  |  |  |  |

REFERENCES

Murphy LJ, Dandy GC, Simpson AR (1994) Optimum design and operation of pumped water distribution systems. In: Conference on Hydraulics in Civil Engineering. Institution of Engineers, Brisbane, pp 149-155

Prasad TD (2010) Design of pumped water distribution networks with storage. J. Water Res. Pl.-ASCE 136: 129-132

# Siew C, Tanyimboh TT, Seyoum AG (2016) Penalty-free multi-objective evolutionary approach to optimization of Anytown water distribution network. Water Resour. Manag. 30: 3671-3688.

Vamvakeridou-Lyroudia LS, Walters GA, Savic DA (2005) Fuzzy multi-objective optimization of water distribution networks. J. Water Res. Pl.-ASCE 131: 467-476

Walters GA, Halhal D, Savic D, Ouazar D (1999) Improved design of “Anytown” distribution network using structured messy genetic algorithms. Urban Water 1: 23-38