Additional file 1

Integration of high-rate filtration using waste-derived biochar as a potential sustainable technology for drinking water supply

Fernando García-Ávila1,2,*, Andrés Galarza-Guamán1, Mónica Barros-Bermeo1, Emigdio Antonio Alfaro Paredes3, Alex Avilés-Añazco1,2,  Sergio Iglesias-Abad4

1 Carrera de Ingeniería Ambiental, Facultad de Ciencias Químicas, Universidad de Cuenca, Ecuador

2 Grupo de Evaluación de Riesgos Ambientales en Sistemas de Producción y Servicios (RISKEN), Departamento de Química Aplicada y Sistemas de Producción, Cuenca, Ecuador.

3Universidad César Vallejo, Professional School of Systems Engineering, Research Institute of Science and Technology, Lima, Peru

4 Carrera de Ingeniería Ambiental, Universidad Católica de Cuenca, Ecuador

∗ Corresponding author.

E-mail address: garcia10f@hotmail.com

List of Additional Information

Table:

Table S1. Effect of the Filtration Rate on the Removal of Physical Parameters for Flocculated Water (Stage 3). (Page S3).

Table S2. Effect of Filtration Rate on the Removal of Physical Parameters for Settled Water (stage 3). (Page S4).

Table S3. Effect of Influent Turbidity on the Removal of Physical Parameters for Raw Water (stage 3). (Page S5).

Table S4. Effect of the Filtration Rate on the Removal of Physical Parameters for Flocculated Water (stage 3). (Page S6)

Table S5. Effect of Filtration Rate on the Removal of Physical Parameters for Settled Water (stage 3). (Page S7)

Table S6. Effect of Influent Turbidity on the Removal of Physical Parameters for Raw Water (stage 3). (Page S8)

Table S7. Turbidity Removal and Robustness Index within Settled Water Treatment. (Page S9)

Table S1. Effect of the Filtration Rate on the Removal of Physical Parameters for Flocculated Water (Stage 3)

| Filter bed | Loading Rate (m3/m2/d) |  | Influent Turbidity |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Low (< 15 NTU) |  | Intermediate (15 – 30 NTU) |  |  |  |  | High (> 30 NTU) |  |  |
| Turbidity removal (%) |  |  |  |  |  |  |  |  |  |  |  |  |
| Ar | 120 | 84.68 ± 21.47 |  | B C | 86.56 ± 25.16 |  |  | B C |  | 95.48 ± 3.80 | E F |  |
|  | 240 | 86.60 ± 11.71 |  | B C | 81.45 ± 31.39 |  |  | B C |  | 68.37 ± 34.69 | B C |  |
| Bc | 120 | 92.23 ± 4.54 |  | C | 95.36 ± 2.23 |  |  | C |  | 98.08 ± 1.61 | F |  |
|  | 240 | 91.59 ± 6.07 |  | C | 96.21 ± 1.30 |  |  | C |  | 91.27 ± 7.80 | D E |  |
| Ca | 120 | 80.67 ± 11.16 |  | B | 85.63 ± 10.18 |  |  | B |  | 91.43 ± 5.53 | C D E |  |
|  | 240 | 81.81 ± 8.64 |  | B | 83.55 ± 8.01 |  |  | A B |  | 75.03 ± 16.25 | B C D |  |
| Gr | 120 | 41.50 ± 23.22 |  | A | 50.34 ± 21.32 |  |  | A |  | 55.80 ± 11.57 | A B |  |
|  | 240 | 34.67 ± 17.04 |  | A | 45.27 ± 20.84 |  |  | A |  | 27.50 ± 14.07 | A |  |
| p value |  |  |  |  |  |  |  |  |  |  |  |
| Effect of filter bed |  |  | < 0.001 * |  | < 0.001 * |  |  |  |  | < 0.001 * |  |  |
| Efecto of loading rate |  |  | 0.607 |  | 0.263 |  |  |  |  | < 0.001 * |  |  |
| Effect of bed x rate |  |  | 0.891 |  | 0.645 |  |  |  |  | 0.052 |  |  |
| Colour removal (%) |  |  |  |  |  |  |  |  |  |  |  |  |
| Ar | 120 | 84.30 ± 22.52 |  | B C |  | 79.48 ± 23.42 |  | B C |  | 91.05 ± 3.03 | E F |  |
|  | 240 | 85.06 ± 13.74 |  | B C |  | 78.87 ± 29.94 |  | B C D |  | 66.11 ± 33.67 | B C |  |
| Bc | 120 | 91.25 ± 9.19 |  | C |  | 88.73 ± 4.35 |  | C D |  | 94.46 ± 2.32 | F |  |
|  | 240 | 90.51 ± 11.82 |  | C |  | 91.96 ± 2.32 |  | D |  | 87.77 ± 7.38 | D E F |  |
| Ca | 120 | 79.07 ± 12 |  | B |  | 79.31 ± 10.53 |  | B |  | 88.09 ± 4.91 | C D E |  |
|  | 240 | 81.03 ± 16.88 |  | B C |  | 79.97 ± 8.26 |  | B |  | 71.73 ± 16.83 | B C D |  |
| Gr | 120 | 49.06 ± 16.28 |  | A |  | 48.52 ± 20.49 |  | A |  | 51.88 ± 10.88 | A B |  |
|  | 240 | 38.94 ± 18.69 |  | A |  | 48.20 ± 11.69 |  | A |  | 25.36 ± 12.72 | A |  |
| p value |  |  |  |  |  |  |  |  |  |  |  |  |
| Effect of filter bed |  |  | < 0.001 * |  | < 0.001 * |  |  |  |  | < 0.001 * |  |  |
| Effect of loading rate |  |  | 0.719 |  | 0.921 |  |  |  |  | < 0.001 * |  |  |
| Effect bed x rate |  |  | 0.673 |  | 0.505 |  |  |  |  | 0.041 * |  |  |
| Values are given as mean ± standard deviation (A B) Means of each column grouped with the same letter are not significantly different (p > 0.05) (*) Significant effect (p < 0.05) |  |  |  |  |  |  |  |  |  |  |  |  |

Table S2. Effect of Filtration Rate on the Removal of Physical Parameters for Settled Water (stage 3)

| Filter bed | Loading Rate (m3/m2/d) | Turbidity removal (%) |  |  |  | Colour removal (%) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ar | 120 |  | 81.27 ± 11.55 | D E |  |  | 78.74 ± 28.44 | E |  |
|  | 240 |  | 61.95 ± 15.67 | B |  |  | 46.23 ± 22.25 | B C |  |
| Bc | 120 |  | 87.53 ± 4.77 | E |  |  | 83.35 ± 20.66 | E |  |
|  | 240 |  | 73.82 ± 13.59 | C D |  |  | 54.23 ± 26.63 | C D |  |
| Ca | 120 |  | 76.91 ± 13.67 | D |  |  | 71.10 ± 33.85 | D E |  |
|  | 240 |  | 63.02 ± 20.39 | B C |  |  | 47.81 ± 27.10 | C |  |
| Gr | 120 |  | 16.80 ± 15.76 | A |  |  | 26.09 ± 34.43 | A B |  |
|  | 240 |  | 16.37 ± 19.45 | A |  |  | 19.99 ± 21.25 | A |  |
| p value |  |  |  |  |  |  |  |  |  |
| Effect of filter bed |  | < 0.001 * |  |  |  |  | < 0.001 * |  |  |
| Effect of loading rate |  | < 0.001 * |  |  |  |  | < 0.001 * |  |  |
| Effect of bed x rate |  | 0.064 |  |  |  |  | 0.007 * |  |  |
| Values are given as mean ± standard deviation |  |  |  |  |  |  |  |  |  |
| (A B) Means of each column grouped with the same letter are not significantly different (p > 0.05) |  |  |  |  |  |  |  |  |  |
| (*) Significant effect (p < 0.05) |  |  |  |  |  |  |  |  |  |

Table S3. Effect of Influent Turbidity on the Removal of Physical Parameters for Raw Water (stage 3)

| Filter bed | Influent Turbidity | Turbidity Removal (%) |  |  |  |  | Colour Removal (%) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 120 m3/m2/d |  |  | 240 m3/m2/d |  | 120 m3/m2/d |  | 240 m3/m2/d |  |
| Ar | Low | 42.40 ± 17.50 |  | B C D | 29.68 ± 22.62 | B C D | 24.27 ± 15.50 | A B C D | 14.74 ± 11.93 | A B C |
|  | Low intermediate | 56.78 ± 23.96 |  | E F G | 40.56 ± 25.17 | C D E | 39.48 ± 26.05 | D E | 26.91 ± 18.59 | C D E F |
|  | High intermediate | 38.62 ± 32.76 |  | C D E | 48.83 ± 25.55 | E F G | 27.54 ± 23.76 | C D | 39.72 ± 21.43 | F G H |
|  | High | 38.57 ± 38.06 |  | C D E | 38.36 ± 34.42 | C D E | 27.22 ± 27.71 | B C D | 30.03 ± 27.42 | C D E F G |
| Bc | Low | 53.67 ± 5.18 |  | D E | 50.95 ± 8.60 | E F G | 34.36 ± 10.89 | D E | 29.66 ± 6.72 | E F G |
|  | Low intermediate | 65.23 ± 6.59 |  | F G H | 61.93 ± 11.48 | F G H | 40.20 ± 6.31 | E F | 41.26 ± 13.39 | G H I |
|  | High intermediate | 67.85 ± 11.31 |  | F G H | 75.55 ± 8.68 | H | 50.05 ± 10.25 | F G | 64.69 ± 12.40 | I |
|  | High | 81.81 ± 7.61 |  | H | 70.49 ± 13.23 | G H | 64.22 ± 13.88 | G | 53.49 ± 14.83 | H I |
| Ca | Low | 43.28 ± 8.05 |  | B C D | 42.83 ± 10.20 | C D E | 25.05 ± 13.51 | A B C D | 21.65 ± 6.12 | B C D E |
|  | Low intermediate | 55.98 ± 5.57 |  | E F | 46.84 ± 9.65 | D E | 32.26 ± 5.62 | C D E | 29.11 ± 10.23 | D E F G |
|  | High intermediate | 58.21 ± 12.85 |  | E F G | 46.92 ± 12.09 | D E F | 40.82 ± 9.62 | E F | 37.79 ± 14.08 | F G H |
|  | High | 70.56 ± 16.36 |  | G H | 57.55 ± 19.22 | E F G H | 53.81 ± 17.17 | F G | 40.55 ± 20.22 | F G H I |
| Gr | Low | 32.52 ± 10.62 |  | A B | 10.56 ± 7.11 | A | 20.19 ± 15.27 | A B C | 4.09 ± 4.88 | A |
|  | Low intermediate | 24.29 ± 12.81 |  | A | 22.04 ± 6.32 | A B | 14.15 ± 7.07 | A | 13.50 ± 4.04 | A B |
|  | High intermediate | 29.50 ± 15.52 |  | A B | 18.61 ± 7.10 | A B | 19.02 ± 10.88 | A B | 21.20 ± 26.63 | A B C D |
|  | High | 39.59 ± 8.04 |  | A B C | 27.26 ± 13.23 | A B C | 25.55 ± 9.50 | A B C D | 15.52 ± 11.75 | A B C |
| p value |  |  |  |  |  |  |  |  |  |  |
| Effect of filter bed |  |  | < 0.001 * |  | < 0.001 * |  | < 0.001 * |  | < 0.001 * |  |
| Effect of influent turbidity |  |  | < 0.001 * |  | < 0.001 * |  | < 0.001 * |  | < 0.001 * |  |
| Effect of bed x turbidity |  |  | < 0.001 * |  | 0.010 * |  | 0.012 * |  | 0.005 * |  |
| Low turbidity (< 20 NTU), low intermediate (20 – 50 NTU), high intermediate (50 – 100 NTU), high (> 100 NTU) Values are given as mean ± standard deviation |  |  |  |  |  |  |  |  |  |  |
| (A B) Means of each column grouped with the same letter are not significantly different (p > 0.05) |  |  |  |  |  |  |  |  |  |  |
| (*) Significant effect (p < 0.05) |  |  |  |  |  |  |  |  |  |  |

Table S4. Effect of the Filtration Rate on the Removal of Physical Parameters for Flocculated Water (stage 3)

| Filter Bed | Loading Rate (m3/m2/d) | Influent Turbidity |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Low (< 15 NTU) |  |  | Intermediate (15 – 30 NTU) |  |  | High (> 30 NTU) |  |  |
| Turbidity Removal (%) |  |  |  |  |  |  |  |  |  |  |
| M1 | 120 | 80.56 ± 13.69 | A |  | 81.01 ± 13.16 | A |  | 92.40 ± 5.29 | A B C |  |
|  | 240 | 76.08 ± 17.59 | A |  | 82.35 ± 8.52 | A |  | 83.10 ± 14.85 | A |  |
| M2 Bc | 120 | 90.21 ± 6.24 | A |  | 86.67 ± 8.24 | A |  | 96.18 ± 2.66 | C |  |
|  | 240 | 85.43 ± 12.70 | A |  | 86.21 ± 11.77 | A |  | 88.72 ± 10.58 | A B C |  |
| M3 Bc | 120 | 87.27 ± 7.15 | A |  | 82.57 ± 13.26 | A |  | 94.70 ± 3.65 | B C |  |
|  | 240 | 82.79 ± 13.27 | A |  | 84.05 ± 6.91 | A |  | 87.11 ± 10.40 | A B |  |
| M4 Bc | 120 | 87.86 ± 7.86 | A |  | 87.32 ± 7.39 | A |  | 95.05 ± 4.66 | C |  |
|  | 240 | 83.66 ± 11.79 | A |  | 85.41 ± 7.37 | A |  | 86.54 ± 10.82 | A B |  |
| p value |  |  |  |  |  |  |  |  |  |
| Effect of filter bed |  | 0.077 |  |  | 0.238 |  |  | 0.345 |  |  |
| Effect of loading rate |  | 0.104 |  |  | 0.961 |  |  | < 0.001 * |  |  |
| Effec of bed x rate |  | 0.990 |  |  | 0.912 |  |  | 0.963 |  |  |
| Colour removal (%) |  |  |  |  |  |  |  |  |  |  |
| M1 | 120 | 76.26 ± 16.15 | A |  | 73.67 ± 17.50 | A |  | 90.89 ± 6.61 | A B C |  |
|  | 240 | 65.50 ± 29.96 | A |  | 79.23 ± 12.64 | A |  | 79.96 ± 16.57 | A |  |
| M2 Bc | 120 | 85.48 ± 9.83 | A |  | 80.23 ± 13.90 | A |  | 95.34 ± 3.66 | C |  |
|  | 240 | 81.58 ± 15.44 | A |  | 85.09 ± 14.26 | A |  | 86.03 ± 11.16 | A B |  |
| M3 Bc | 120 | 82.34 ± 10.85 | A |  | 74.88 ± 17.89 | A |  | 94.20 ± 3.47 | B C |  |
|  | 240 | 83.75 ± 12.58 | A |  | 81.41 ± 12.01 | A |  | 83.26 ± 12.60 | A |  |
| M4 Bc | 120 | 84.76 ± 10.83 | A |  | 80.77 ± 13.51 | A |  | 93.95 ± 5.95 | C |  |
|  | 240 | 80.52 ± 17.65 | A |  | 84.52 ± 7.63 | A |  | 83.43 ± 12.21 | A |  |
| p value |  |  |  |  |  |  |  |  |  |  |
| Effect of filter bed |  | 0.175 |  |  | 0.394 |  |  | 0.387 |  |  |
| Effect of loading rate |  | 0.558 |  |  | 0.109 |  |  | < 0.001 * |  |  |
| Effect of bed x rate |  | 0.824 |  |  | 0.979 |  |  | 0.985 |  |  |
| (Bc) Filter bed with biochar Values are given as mean ± standard deviation (A B) Means of each column grouped with the same letter are not significantly different (p > 0.05) (*) Significant effect (p < 0.05) |  |  |  |  |  |  |  |  |  |  |

Table S5. Effect of Filtration Rate on the Removal of Physical Parameters for Settled Water (stage 3)

| Filter Bed | Loading Rate (m3/m2/d) | Turbidity Removal (%) |  |  | Colour Removal (%) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| M1 | 120 | 74.49 ± 5.92 |  | A B |  | 73.31 ± 23.10 |  | A B |
|  | 240 | 71.62 ± 7.95 |  | A |  | 65.69 ± 20.60 |  | A |
| M2 Bc | 120 | 80.34 ± 5.44 |  | C D |  | 87.72 ± 15.76 |  | C |
|  | 240 | 79.55 ± 6.55 |  | C D |  | 78.86 ± 21.16 |  | B C |
| M3 Bc | 120 | 78.83 ± 5.70 |  | B C D |  | 80.26 ± 18.16 |  | B C |
|  | 240 | 76.09 ± 6.91 |  | A B C |  | 78.70 ± 18.16 |  | B |
| M4 Bc | 120 | 81.78 ± 5.50 |  | D |  | 87.93 ± 14.80 |  | C |
|  | 240 | 78.12 ± 6.42 |  | B C D |  | 83.93 ± 15.92 |  | B C |
| p value |  |  |  |  |  |  |  |  |
| Effect of filter bed |  | < 0.001 * |  |  |  | < 0.001 * |  |  |
| Effect of loading rate |  | 0.002 * |  |  |  | 0.004 * |  |  |
| Effect of bed x rate |  | 0.646 |  |  |  | 0.574 |  |  |
| (Bc) Filter bed with biochar Values are given as mean ± standard deviation |  |  |  |  |  |  |  |  |
| (A B) Means of each column grouped with the same letter are not significantly different (p > 0.05) |  |  |  |  |  |  |  |  |
| (*) Significant effect (p < 0.05) |  |  |  |  |  |  |  |  |

Table S6. Effect of Influent Turbidity on the Removal of Physical Parameters for Raw Water (stage 3)

| Filter Bed | Influent Turbidity | Turbidity Removal (%) |  |  |  |  | Colour Removal (%) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 120 m3/m2/d |  |  | 240 m3/m2/d |  | 120 m3/m2/d |  | 240 m3/m2/d |  |
| M1 | Low | 60.18 ± 9.68 |  | A | 59.91 ± 5.13 | A | 36.88 ± 9.82 | A | 34.14 ± 11.01 | A |
|  | Low intermediate | 66.46 ± 7.07 |  | A B C D | 68.95 ± 9.10 | B C | 43.33 ± 7.44 | A B C D | 41.37 ± 16.34 | A B |
|  | High intermediate | 70.98 ± 13.30 |  | C D E F | 70.87 ± 6.90 | C D | 54.49 ± 14.98 | E F G | 48.58 ± 8.44 | B C D E |
|  | High | 89.29 ± 11.17 |  | G | 85.32 ± 18.62 | D E | 77.25 ± 15.77 | H | 74.16 ± 21.94 | E F |
| M2 Bc | Low | 62.13 ± 10.49 |  | A B | 63.51 ± 4.22 | A B | 39.48 ± 8.90 | A B | 42.28 ± 7.80 | A B C D |
|  | Low intermediate | 69.57 ± 6.36 |  | B C D E | 72.93 ± 8.44 | C D E | 46.15 ± 10.11 | B C D E | 46.79 ± 15.47 | A B C D |
|  | High intermediate | 76.81 ± 9.72 |  | E F G | 73.10 ± 8.82 | C D E | 60.34 ± 11.96 | G H | 51.50 ± 11.44 | C D E F |
|  | High | 73.53 ± 37.70 |  | F G | 88.12 ± 16.78 | E | 64.56 ± 35.10 | G H | 78.41 ± 20.40 | F |
| M3 Bc | Low | 63.12 ± 6.54 |  | A B | 62.37 ± 4.16 | A B | 40.89 ± 7.64 | A B C | 40.60 ± 6.89 | A B C |
|  | Low intermediate | 71.54 ± 5.40 |  | D E F | 72.66 ± 8.00 | C D E | 49.03 ± 8.36 | D E F G | 46.27 ± 15.17 | A B C D |
|  | High intermediate | 75.29 ± 9.37 |  | E F G | 74.13 ± 5.94 | C D E | 58.46 ± 12.69 | F G H | 51.80 ± 8.10 | D E F |
|  | High | 73.07 ± 37.68 |  | E F G | 85.14 ± 20.97 | D E | 64.38 ± 35.39 | G H | 75.68 ± 22.80 | E F |
| M4 Bc | Low | 64.17 ± 6.27 |  | A B C | 61.61 ± 4.32 | A B | 43.81 ± 7.87 | A B C D | 40.02 ± 7.25 | A B |
|  | Low intermediate | 70.33 ± 7.18 |  | D E F | 72.27 ± 8.07 | C D E | 48.13 ± 9.37 | C D E F | 46.85 ± 14.72 | B C D |
|  | High intermediate | 74.42 ± 10.13 |  | E F G | 73.55 ± 5.87 | C D E | 56.62 ± 13.25 | E F G H | 49.92 ± 9.51 | B C D E |
|  | High | 72.43 ± 37.65 |  | E F G | 86.09 ± 20.62 | D E | 63.48 ± 35.60 | F G H | 76.14 ± 23.79 | E F |
| p value |  |  |  |  |  |  |  |  |  |  |
| Effect of filter bed |  |  | 0.920 |  | 0.570 |  | 0.909 |  | 0.494 |  |
| Effect of influent turbidity |  |  | < 0.001 * |  | < 0.001 * |  | < 0.001 * |  | < 0.001 * |  |
| Effect of bed x turbidity |  |  | 0.861 |  | 0.999 |  | 0.841 |  | 0.999 |  |
| Low turbidity (< 20 NTU), low intermediate (20 – 50 NTU), high intermediate (50 – 100 NTU), high (> 100 NTU) (Bc) Filter bed with biochar Values are given as mean ± standard deviation |  |  |  |  |  |  |  |  |  |  |
| (A B) Means of each column grouped with the same letter are not significantly different (p > 0.05) |  |  |  |  |  |  |  |  |  |  |
| (*) Significant effect (p < 0.05) |  |  |  |  |  |  |  |  |  |  |

Table S7. Turbidity Removal and Robustness Index within Settled Water Treatment

| Filter Bed | Loading Rate (m3/m2/d) | Turbidity Removal (%) |  | T50 (NTU) | T95 (NTU) | TRI95 |
| --- | --- | --- | --- | --- | --- | --- |
| Ar | 120 | 81.27 ± 11.55 | F | 0.25 | 0.57 | 1.39 |
|  | 240 | 61.95 ± 15.67 | B | 0.72 | 1.01 | 1.42 |
| Bc | 120 | 87.53 ± 4.77 | G | 0.21 | 0.36 | 1.07 |
|  | 240 | 73.82 ± 13.59 | C D E | 0.39 | 0.84 | 1.47 |
| Ca | 120 | 76.91 ± 13.67 | D E F | 0.35 | 0.73 | 1.4 |
|  | 240 | 63.02 ± 20.39 | B C | 0.56 | 1.08 | 1.52 |
| Gr | 120 | 16.8 ± 15.76 | A | 1.54 | 2.45 | 2.33 |
|  | 240 | 16.37 ± 19.45 | A | 1.6 | 6.6 | 3.66 |
| M1 | 120 | 74.49 ± 5.92 | B C D | 0.29 | 0.35 | 0.89 |
|  | 240 | 71.62 ± 7.95 | B C | 0.34 | 0.52 | 1.1 |
| M2 | 120 | 80.34 ± 5.44 | E F | 0.22 | 0.3 | 0.89 |
|  | 240 | 79.55 ± 6.55 | E F | 0.2 | 0.3 | 0.95 |
| M3 | 120 | 78.83 ± 5.7 | D E F | 0.24 | 0.29 | 0.85 |
|  | 240 | 76.09 ± 6.91 | C D E | 0.22 | 0.42 | 1.16 |
| M4 | 120 | 81.78 ± 5.5 | F | 0.19 | 0.3 | 0.98 |
|  | 240 | 78.12 ± 6.42 | D E F | 0.22 | 0.41 | 1.17 |
| Turbidity removal is given as mean ± standard deviation (A B) Means grouped with the same letter are not significantly different (p > 0.05) |  |  |  |  |  |  |