Supplementary material

APPENDIX-1

Heat loss calculation for government Guest house

Table 5 Heat loss calculation for walls

| Wall |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sr. no | Parameters | size | unit | formula |
|  | Wall thickness | 0.3 | M |  |
|  | Heat conductivity | 0.69 | W/m/°C |  |
|  | Convection inside | 5 | W/m2/°C |  |
|  | Convection outside | 25 | W/m2/°C |  |
|  | R_inside | 0.2 | m2 °C/W | = (1/convection inside) |
|  | R_outside | 0.04 | m2 °C/W | = (1/convection outside) |
|  | R_wall_material | 0.4348 | m2 °C/W | = (wall thickness/ wall Conductivity) |
|  | R_total | 0.6748 | m2 °C/W | =(R_inside+R_outside+R_wall material) |
|  | U_wall | 1.4820 | W/m2/°C | =(1/R_Total) |
| Floor |  |  |  |  |
|  | U_floor (20% of U_wall) | 0.2964 | W/m2/°C | =U_Wall˟0.2 |

Table 6: Heat loss calculation for roof

| Roof |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sr. no | Parameters | size | unit | formula |
|  | Roof thickness | 0.003 | m |  |
|  | Heat conductivity | 79.5 | W/m/°C |  |
|  | Convection inside | 8 | W/m2/°C |  |
|  | Convection outside | 25 | W/m2/°C |  |
|  | R_inside | 0.125 | m2 °C/W | = (1/convection inside) |
|  | R_outside | 0.04 | m2 °C/W | = (1/convection outside) |
|  | R_roof_material | 0.0000377 | m2 °C/W | = (wall thickness/ wall Conductivity) |
|  | R_total | 0.1650 | m2 °C/W | =(R_inside+R_outside+R_wall material) |
|  | U_roof guesthouse est. 2xU_wall | 2.9639 | W/m2/°C | =(1/R_Total) |

Table 7: Heat loss calculation for window

| Window |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sr. no | Parameters | size | unit | formula |
|  | Window thickness | 0.006 | m |  |
|  | Heat conductivity | 0.96 | W/m/°C |  |
|  | Convection inside | 8 | W/m2/°C |  |
|  | Convection outside | 25 | W/m2/°C |  |
|  | R_inside | 0.125 | m2 °C/W | = (1/convection inside) |
|  | R_outside | 0.04 | m2 °C/W | = (1/convection outside) |
|  | R_window_material | 0.0063 | m2 °C/W | = (wall thickness/ wall Conductivity) |
|  | R_total | 0.1713 | m2°C/W | =(R_inside+R_outside+R_wall material) |
|  | U_window | 5.8394 | W/m2/°C | =(1/R_Total) |

Table 8 : Details of the government guesthouse ( proposed site for house heating system)

| government Guest house and other essential details |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sr. no | Parameters | size | unit | formula |
|  | Length | 50 | m |  |
|  | Width | 20 | m |  |
|  | Height | 8 | m |  |
|  | Area | 1000.0 | m2 | = length ˟ Width |
|  | Volume | 8000.0 | m3 | = length ˟ Width˟Height |
|  | Horizontal perimeter | 140 | m |  |
|  | Of that, windows 4.5+6.7+3 | 14.2 | m |  |
|  | Window area | 113.6 | m2 | =Height of the GH ˟ Of that, windows 4.5+6.7+3 |
|  | Wall area | 1006.4 | m2 | =(Horizontal perimeter- Of that, windows 4.5+6.7+3) ˟ Height of the GH |
|  | Total window+wall area | 1120.0 | m2 | =(window area+wall area) |
|  | Indoor temp. | 20 | °C |  |
|  | Outdoor temp. | -10 | °C |  |
|  | Air change rate | 2 | 1/h |  |

Table 9: Total heat demand for heating the government guest house

| Sr. No | Perimeter | Value | Unit | Formula | Area (m2) | Transmission loss (W) | Formula |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Wall | 1.48 | m2 °C/W | U_Wall | 1006.40 | 44,743 | =(Wall ˟ wall area) ˟(indoor temperature- outdoor temperature) |
|  | Floor | 0.29 |  | U_floor (20% of U_wall) | 1000.0 | 8,892 | =(Floor˟ Floor area) ˟(indoor temperature- outdoor temperature) |
|  | Roof | 2.96 |  | U_roof guesthouse est. 2xU_wall | 1000.0 | 88,918 | =(Roof ˟ Roof area) ˟(indoor temperature- outdoor temperature) |
|  | Window | 5.83 |  | U_window | 113.60 | 19,901 | =(window ˟ window area) ˟(indoor temperature- outdoor temperature) |
|  | Total transmission losses |  |  |  |  | 1,62,453 | =( Wall+ Floor+ Roof+ Window) |
|  | guesthouse volume | 8000.0 | m3 |  |  |  |  |
|  | Air density | 1.1774 | kg/m3 |  |  |  |  |
|  | Air heat capacity (cp) | 1,006 | J/kg/°C |  |  |  |  |
|  | Mass of air | 9419.20 | kg | =(house volume ˟ air density |  |  |  |
|  | Air change heat demand |  |  |  |  | 1,57,929 | ={mass of air ˟(air change rate ˟3600) ˟air heat capacity ˟(indoor temperature-outdoor temperature)} |
|  | Total heat demand |  |  |  |  | 3,20,382 Watt | =(total transmission loss+air change heat demand) |
|  | Heat demand W/m2 (area) |  |  |  |  | 320 | =(total heat demand/ area of the guesthouse |
|  | Heat demand W/m2 (volume) |  |  |  |  | 40 | =(total heat demand/ volume of the guesthouse |

Energy exchange calculations:

Table 10 Input parameter for  heat transfer estimation

| Sr. No | Assumption | Value | Unit | Formula |
| --- | --- | --- | --- | --- |
|  | Geothermal water temperature from the hot spring | 55.5 | °C |  |
|  | Geothermal water temperature from the heat exchanger | 30 | °C |  |
|  | Radiator water temperature from the heat exchanger | 50 | °C |  |
|  | Radiator water temperature to the heat exchanger | 35 | °C |  |
|  | Total heat demand | 3,20,382 | W |  |

Table 11 Heat transfer in the heat exchanger

| Geothermal Water |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sr. No | Parameters | Values | Unit | Formula |
|  | Q_ (heat demand) | 3,20,382 | W |  |
|  | Cp_ (specific heat capacity of water) | 4,200 | J/kg/°C |  |
|  | T1 _(inlet temp. to the heat exchanger) | 55.5 | °C |  |
|  | T2_ (outlet temp. from the heat exchanger) | 30 | °C |  |
|  | m _(geothermal water mass flow through the heat exchanger) | 2.99 | kg/s | = heat demand/specific heat capacity of water/(Inlet temp . – Outlet temp.) |
| Radiator Water |  |  |  |  |
|  | Q (heat demand) | 3,20,382 | W |  |
|  | cp (specific heat capacity of water) | 4,200 | J/kg/°C |  |
|  | T1 (outlet temp from the heat exchanger) | 50 | °C |  |
|  | T2 (inlet temp. to the heat exchanger) | 35 | °C |  |
|  | m (radiator water mass flow through the heat exchanger) | 5.09 | kg/s | =Heat demand/ specific heat of water/(Outlet temperature- Inlet temperature). |