Supplementary Information

Integrated Digital Twin and Deep Reinforcement Learning Framework for Climate-Adaptive Building Energy Optimization: A Graph Neural Network Approach for Extreme Hot-Arid Environments

Table of Contents

- S1. Detailed Mathematical Formulations

- S2. Digital Twin Model Specifications and Calibration

- S3. Graph Neural Network Architecture Details

- S4. Deep Reinforcement Learning Hyperparameters and Training

- S5. Dust Storm Forecasting Module

- S6. Climate Data Analysis

- S7. Building Characteristics and Instrumentation

- S8. Extended Validation Results

- S9. Transfer Learning Analysis

- S10. Computational Infrastructure and Deployment

- S11. Economic Analysis Details

- S12. Sensitivity Analysis

- S13. Building-Level Savings Distribution and Confidence Intervals

- S14. Community-Scale Simulation Methodology

- S15. Monte Carlo Uncertainty Propagation Analysis

S1. Detailed Mathematical Formulations

This section provides comprehensive mathematical formulations that are summarized in the main manuscript.

S1.1. Thermal Resistance-Capacitance Network

The building thermal model is formulated based on a fourth-order resistance-capacitance network. The system state equations are defined as follows:

CzdTzdt=Tw,i-TzRi+QHVAC+Qint+Qsol,z

Cw,idTw,idt=Tz-Tw,iRi+Tw,o-Tw,iRw

Cw,odTw,odt=Tw,i-Tw,oRw+Tout-Tw,oRo+Qsol,w

CrdTrdt=Tout-TrRr+Tz-TrRr,i+Qsol,r

where Cz, Cw,i, Cw,o, and Crrepresent the thermal capacitances of the interior zone, interior wall, exterior wall, and roof, respectively. Ri, Rw, Ro, Rr, and Rr,idenote the corresponding thermal resistances. QHVACrepresents the HVAC thermal load, Qintdenotes internal heat gains, and Qsol,z, Qsol,w, and Qsol,rrepresent solar radiation loads incident on each node.

S1.2. COP Degradation Model Under Dust Conditions

The coefficient of performance degradation model under dust storm conditions is formulated as:

COP(t)=COPnom⋅ηT(Tout)⋅ηdust(PM10)⋅ηage

ηT(Tout)=1-αT(Tout-Tref)βT

ηdust(PM10)=11+γdPM10PMrefδd

where COPnomdenotes the nominal coefficient of performance, ηTrepresents the temperature correction factor with parameters αT=0.018and βT=1.12at reference temperature Tref=35°C, and ηdustrepresents the dust correction factor with γd=0.42and δd=0.89at reference concentration PMref=150  μg/m3. ηagedenotes the equipment degradation factor with a default value of 0.95 for five-year-old systems.

S1.3. Multi-Objective Reward Function

The multi-objective reward function for the deep reinforcement learning agent is defined as:

r(t)=-ωe⋅renergy(t)+ωc⋅rcomfort(t)+ωp⋅rpeak(t)+ωs⋅rstorm(t)

renergy(t)=PHVAC(t)Pmax

rcomfort(t)=max⁡0  ∣Tz(t)-Tset(t)∣-ΔTdbΔTmax2

rpeak(t)=max⁡0  PHVAC(t)-PthresholdPmax

rstorm(t)=λpre⋅1[t∈Tpre]⋅max⁡0,  Tz(t)-Tpre

where ωe=0.40, ωc=0.35, ωp=0.15, and ωs=0.10represent the weights for each component. ΔTdb=0.5°Cdenotes the comfort deadband, ΔTmax=4.0°Crepresents the maximum allowable deviation, Pthresholddenotes the peak load threshold, and Tprerepresents the pre-cooling target temperature. 1[t∈Tpre]is the indicator function for the storm pre-cooling period, and λpre=2.0represents the pre-cooling penalty amplification factor.

S1.4. GNN Message Passing Formulation

The message passing mechanism in the graph neural network is formulated as:

mi→jl=ϕelhilhjleij

mjl=i∈N(j)αijl⋅mi→jl

hjl1=ϕvlhjlmjl

αijl=expLeakyReLUal)T[Wlhil∥Wlhjl]k∈N(j)exp⁡LeakyReLUal)T[Wlhkl∥Wlhjl]

where hilrepresents the feature vector of node iat layer l, eijdenotes the edge feature between nodes iand j, N(j)represents the neighbor set of node j, ϕeland ϕvldenote edge and node functions parameterized by neural networks, αijlrepresents attention coefficients, Wldenotes the weight matrix, and alrepresents the attention vector.

S2. Digital Twin Model Specifications and Calibration

| Table S1. Digital Twin Calibration Parameters and Validation Metrics |  |  |  |  |
| --- | --- | --- | --- | --- |
| Parameter | Residential | Commercial | Unit | Calibration Method |
| Cz(Zone Thermal Capacitance) | 2.8 | 8.5 | MJ/°C | Bayesian Optimization |
| Cw,i(Interior Wall Capacitance) | 1.4 | 3.2 | MJ/°C | Bayesian Optimization |
| Cw,o(Exterior Wall Capacitance) | 3.1 | 6.8 | MJ/°C | Bayesian Optimization |
| Cr(Roof Capacitance) | 1.9 | 4.1 | MJ/°C | Bayesian Optimization |
| Ri(Interior Surface Resistance) | 0.12 | 0.08 | °C/W | In-situ Measurement |
| Rw(Wall Core Resistance) | 0.45 | 0.38 | °C/W | In-situ Measurement |
| Ro(Exterior Surface Resistance) | 0.06 | 0.05 | °C/W | Empirical Correlation |
| Rr(Roof Resistance) | 0.52 | 0.41 | °C/W | In-situ Measurement |
| RMSE (Validation) | 0.55 | 0.66 | °C | 30-day Holdout Test |
| R2(Validation) | 0.941 | 0.928 | — | 30-day Holdout Test |
| CVRMSE | 4.2 | 5.1 | % | ASHRAE Guideline 14 |
| Calibration Data Period | 90 | 90 | days | — |
| Number of Calibration Parameters | 14 | 18 | — | — |
| Bayesian Optimization Iterations | 500 | 500 | — | Expected Improvement |

S3. Graph Neural Network Architecture Details

| Table S2. GNN Architecture Specifications |  |  |
| --- | --- | --- |
| Component | Specification | Notes |
| Architecture Type | Graph Attention Network (GAT) | Multi-head attention mechanism |
| Number of GNN Layers | 3 | With residual connections |
| Hidden Dimension | 128 | Per layer |
| Attention Heads | 4 | Concatenated in layers 1-2, averaged in layer 3 |
| Node Feature Dimension (Input) | 23 | Per building |
| Edge Feature Dimension | 5 | Distance, orientation, type similarity, thermal correlation, shared infrastructure |
| Node Feature Components | Tz, Tw,i, Tw,o, Tr, Tout, RH, SR, WS, WD, PM10, PHVAC, COP, Tset, Occ, Occpred, DoW, HoD, Ecum, Ppeak, ΔT/Δt, Stormprob, StormETA, Tpre,status | 23 features total |
| Activation Function | ELU | Between layers |
| Dropout Rate | 0.1 | Applied after attention |
| Layer Normalization | Applied | After each GNN layer |
| Graph Construction | k-NN with k=5 | Based on physical proximity |
| Maximum Graph Radius | 500 m | Euclidean distance threshold |
| Attention Temperature | 0.1 | Sharpening factor |
| Output Embedding Dimension | 64 | Fed to policy and value heads |

S4. Deep Reinforcement Learning Hyperparameters and Training

| Table S3. DRL Training Configuration and Hyperparameters |  |  |
| --- | --- | --- |
| Hyperparameter | Value | Selection Method |
| Algorithm | SAC (Soft Actor-Critic) | Comparative evaluation |
| Discount Factor (γ) | 0.99 | Standard for long-horizon tasks |
| Learning Rate (Actor) | 3×10-4 | Grid search |
| Learning Rate (Critic) | 3×10-4 | Grid search |
| Learning Rate (Temperature α) | 1×10-4 | Automatic tuning |
| Batch Size | 256 | Memory-performance tradeoff |
| Replay Buffer Size | 1×106 | Per agent |
| Target Network Update (τ) | 0.005 | Soft update |
| Initial Temperature (α0) | 0.2 | Auto-tuned |
| Actor Network | [256, 256, 128] | MLP layers after GNN embedding |
| Critic Network | [256, 256, 128] | Twin Q-networks |
| Action Dimension | 3 | Tset, fan speed, mode |
| Action Range (Tset) | [20, 28] °C | Comfort-constrained |
| State Dimension (per agent) | 23 + 64 (GNN) = 87 | Local observation + GNN embedding |
| Training Episodes | 5000 | Convergence criterion |
| Steps per Episode | 288 | 24 hours at 5-minute intervals |
| Warm-up Steps | 10000 | Random exploration |
| Gradient Clipping | 1.0 | Maximum norm |
| Reward Normalization | Running mean/std | Updated online |
| Exploration Noise | Entropy-based (SAC) | Automatic |
| Convergence Criterion | < 1% reward change over 100 episodes | Early stopping |
| Training Wall-Clock Time | 18.5 hours | 8-building configuration |

S5. Dust Storm Forecasting Module

| Table S4. Dust Storm Forecasting Module Specifications |  |  |
| --- | --- | --- |
| Component | Specification | Details |
| Forecasting Architecture | Hybrid CNN-LSTM | Two-stage pipeline |
| CNN Component | ResNet-18 backbone | Pre-trained on satellite imagery |
| CNN Input | 64×64satellite patches | MODIS AOD products, 15-minute update |
| LSTM Hidden Units | 128 | 2-layer stacked |
| LSTM Input Sequence | 24 time steps | 6-hour lookback at 15-minute intervals |
| LSTM Features | PM10, visibility, wind speed, wind direction, pressure, humidity, AOD | 7 features per time step |
| Fusion Layer | Fully connected [256, 128, 64] | CNN + LSTM concatenation |
| Output Heads | Storm probability, ETA, expected duration, peak PM10 | 4 outputs |
| Storm Probability Threshold | 0.65 | For pre-cooling activation |
| Training Data | 3 years historical | 47 confirmed dust events |
| Validation Approach | Leave-one-storm-out | Cross-validation |
| Onset Detection Accuracy | 91.3% | At 2-hour lead time |
| ETA Mean Absolute Error | 18 min | For confirmed events |
| Duration Prediction RMSE | 42 min | For events exceeding 2 hours |
| Peak PM10Prediction MAPE | 15.7% | Relative error |
| False Positive Rate | 8.7% | At 0.65 threshold |
| Pre-cooling Lead Time | 2.0 to 2.5 hours | Adaptive based on building thermal mass |

S6. Climate Data Analysis

| Table S5. Climate Conditions and Environmental Statistics |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Parameter | Summer Mean | Summer Peak | Dust Storm Mean | Dust Storm Peak | Transition Period | Unit |
| Outdoor Temperature | 44.2 | 51.8 | 46.1 | 52.3 | 35.2 (evening low) | °C |
| Relative Humidity | 18.5 | 42.0 | 12.3 | 8.5 | 28.6 | % |
| Solar Radiation | 892 | 1,080 | 340 | 120 | 0 (night) | W/m² |
| Wind Speed | 3.8 | 12.5 | 14.2 | 28.6 | 4.1 | m/s |
| PM10Concentration | 185 | 420 | 1,850 | 4,200 | 165 | μg/m3 |
| Diurnal Temperature Range | 16.0 | 19.5 | 11.2 | 14.0 | 16.0 | °C |
| Dust Events (Annual) | — | — | 23.4 | — | — | events/year |
| Mean Dust Event Duration | — | — | 4.8 | 14.2 | — | hours |
| Cooling Degree Days (Annual) | 3,847 | — | — | — | — | °C·day |
| Prevailing Wind Direction | NW (315°) | — | NW-W (290°-320°) | — | Variable | degrees |
| Sky Clearness Index | 0.72 | 0.81 | 0.25 | 0.08 | 0.68 | — |
| Atmospheric Pressure | 1008.2 | 1015.0 | 1003.5 | 998.0 | 1009.0 | hPa |

S7. Building Characteristics and Instrumentation

| Table S6. Building Portfolio Specifications and Sensor Deployment |  |  |  |
| --- | --- | --- | --- |
| Characteristic | Residential (6 units) | Commercial (3 units) | Unit |
| Floor Area (mean ± std) | 285 ± 62 | 1,450 ± 380 | m² |
| Number of Floors | 2 to 3 | 4 to 8 | — |
| Construction Year | 2008 to 2016 | 2012 to 2019 | — |
| Wall U-value | 0.42 ± 0.08 | 0.35 ± 0.05 | W/m²·°C |
| Roof U-value | 0.38 ± 0.06 | 0.30 ± 0.04 | W/m²·°C |
| Window-to-Wall Ratio | 0.25 ± 0.05 | 0.40 ± 0.08 | — |
| Window U-value | 2.4 ± 0.3 | 1.8 ± 0.2 | W/m²·°C |
| SHGC (Solar Heat Gain Coefficient) | 0.35 ± 0.05 | 0.25 ± 0.03 | — |
| HVAC Type | Split/Multi-split | Centralized VAV | — |
| Nominal Cooling Capacity | 14.0 ± 3.5 | 120 ± 35 | kW |
| Nominal COP | 3.2 ± 0.3 | 4.1 ± 0.4 | — |
| HVAC Capacity per Volume | 18.5 | 42.8 | W/m³ |
| Temperature Sensors per Building | 6 ± 2 | 18 ± 5 | — |
| Power Meters per Building | 2 | 5 | — |
| Occupancy Sensors per Building | 3 ± 1 | 8 ± 2 | PIR + CO₂ |
| PM10Sensors | 1 (shared outdoor) | 1 (shared outdoor) | per cluster |
| Weather Station | 1 (shared) | 1 (shared) | per deployment |
| Data Acquisition Interval | 5 | 5 | minutes |
| Communication Protocol | MQTT over Wi-Fi | BACnet/IP | — |
| Edge Computing Device | NVIDIA Jetson Nano | NVIDIA Jetson Xavier NX | — |

S8. Extended Validation Results

| Table S7. Comprehensive Performance Comparison Across Methods and Conditions |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Metric | Proposed Framework | MPC | RBC (Optimized) | Default Schedule | Condition |
| Energy Savings (%) | 38.7 | 24.1 | 12.3 | Baseline | Normal Summer |
| Energy Savings (%) | 41.8 | 26.8 | 14.1 | Baseline | Normal (Commercial) |
| Energy Savings (%) | 36.5 | 22.3 | 11.0 | Baseline | Normal (Residential) |
| Energy Savings (%) | 45.3 | 28.9 | 8.7 | Baseline | Dust Storm |
| Energy Savings (%) | 44.2 | 27.5 | 9.2 | Baseline | Dust Storm (Residential) |
| Energy Savings (%) | 46.8 | 30.8 | 7.9 | Baseline | Dust Storm (Commercial) |
| Comfort Compliance (%) | 98.2 | 97.8 | 94.5 | 91.2 | Normal Summer |
| Comfort Compliance (%) | 96.7 | 95.1 | 88.3 | 82.6 | Dust Storm |
| Peak Load Reduction (%) | 22.4 | 15.6 | 8.9 | Baseline | Normal Summer |
| Peak Load Reduction (%) | 31.2 | 18.3 | 5.2 | Baseline | Dust Storm |
| Mean Temperature Deviation | 0.31 | 0.38 | 0.82 | 1.15 | °C (Normal) |
| Mean Temperature Deviation | 0.48 | 0.65 | 1.45 | 2.10 | °C (Dust Storm) |
| Max Temperature Excursion | 1.8 | 2.3 | 3.8 | 5.2 | °C (Dust Storm) |
| Recovery Time After Storm | 23 | 38 | 67 | 95 | minutes |
| Pre-cooling Energy Overhead | 8.2 | 12.5 | N/A | N/A | % of daily consumption |
| Coordination Benefit (GNN) | 9.8 | N/A | N/A | N/A | % additional savings |

S9. Transfer Learning Analysis

| Table S8. Transfer Learning Performance and Convergence Analysis |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Transfer Scenario | Convergence Speedup | Final Performance Gap | KL Divergence (Temperature) | KL Divergence (Occupancy) | Shared Encoder Layers Frozen | Fine-tuning Episodes |
| Residential → Commercial | 38% faster | 1.2% lower | 0.31 | 0.52 | GNN layers 1-2 | 1,850 |
| Commercial → Residential | 29% faster | 2.1% lower | 0.31 | 0.52 | GNN layers 1-2 | 2,200 |
| Old Residential → New Residential | 52% faster | 0.4% lower | 0.18 | 0.21 | GNN layers 1-3 | 1,100 |
| Small Commercial → Large Commercial | 41% faster | 1.5% lower | 0.24 | 0.15 | GNN layers 1-2 | 1,500 |
| 8-building → 50-building | 45% faster | 0.8% lower | 0.22 | 0.31 | Full GNN encoder | 2,800 |
| 8-building → 150-building | 43% faster | 1.1% lower | 0.25 | 0.34 | Full GNN encoder | 3,200 |
| Summer → Shoulder Season | 33% faster | 3.2% lower | 0.45 | 0.38 | GNN layer 1 only | 2,600 |
| Without Transfer (Baseline) | — | Reference | — | — | None |  |

S10. Computational Infrastructure and Deployment

| Table S9. Computational Infrastructure Specifications |  |  |  |
| --- | --- | --- | --- |
| Component | Training Phase | Deployment Phase (Edge) | Deployment Phase (Cloud) |
| Hardware | NVIDIA A100 (80GB) × 2 | NVIDIA Jetson Nano/Xavier NX | AWS EC2 g4dn.xlarge |
| CPU | AMD EPYC 7763 (64-core) | ARM Cortex-A57 (Nano) / Carmel (Xavier) | 4 vCPUs |
| RAM | 512 GB | 4 GB (Nano) / 8 GB (Xavier) | 16 GB |
| Storage | 2 TB NVMe SSD | 64 GB microSD | 125 GB SSD |
| Framework | PyTorch 2.1 + PyG 2.4 | PyTorch Mobile + TensorRT | PyTorch 2.1 |
| Inference Latency | N/A | 145 ms (Nano) / 82 ms (Xavier) | 35 ms |
| Control Cycle | N/A | 5 minutes | 5 minutes (backup) |
| Power Consumption | 600 W (total system) | 10 W (Nano) / 15 W (Xavier) | N/A |
| Network Requirement | N/A | Wi-Fi / Ethernet (< 1 Mbps) | Internet (< 5 Mbps) |
| Model Size (compressed) | N/A | 12.4 MB (per agent) | 18.7 MB (full) |
| OS | Ubuntu 22.04 | JetPack 5.1 (L4T) | Amazon Linux 2 |
| Training Time (8 buildings) | 18.5 hours | N/A | N/A |
| Training Time (150 buildings) | 72 hours | N/A | N/A |
| Failover Mechanism | N/A | Local rule-based fallback | Cloud-to-edge sync |

S11. Economic Analysis Details

| Cost/Benefit Item | Residential (per unit) | Commercial (per unit) | Unit | Notes |
| --- | --- | --- | --- | --- |
| Edge Computing Hardware | 450 | 850 | USD | Jetson Nano vs Xavier NX |
| Temperature and Environmental Sensors | 360 | 1,080 | USD | 6 vs 18 sensors at 60 USD each |
| Power Meters | 300 | 750 | USD | 2 vs 5 meters at 150 USD each |
| Occupancy Sensors (PIR + CO₂) | 270 | 720 | USD | 3 vs 8 sensors at 90 USD each |
| Installation Labor | 800 | 2,200 | USD | Wiring, mounting, physical setup |
| Commissioning and Testing Labor | 250 | 400 | USD | System startup, control verification |
| Shared Instrumentation Allocation | 210 | 260 | USD | Prorated weather station and PM10 monitor |
| Cybersecurity Setup and First-Year License | 190 | 280 | USD | Encryption, authentication configuration |
| Software License (first year) | 120 | 350 | USD | Cloud services and updates |
| Cloud Computing Infrastructure Setup | 260 | 340 | USD | First-year hosting, prorated |
| HVAC Interface Retrofit (portfolio average) | 750 | 400 | USD | Averaged across legacy and modern units |
| Digital Twin Calibration and Control Engineering | 3,460 | 1,700 | USD | One-time, Bayesian calibration and MCMC engineering effort |
| Contingency and Project Management (approx. 10%) | 780 | 470 | USD | — |
| Total Deployment Cost (fully loaded) | 8,200 | 9,800 | USD | Matches portfolio-average investment in Table 3 |
| Annual Energy Savings | 3,520 | 6,340 | USD | Matches Table 3 |
| Annual Maintenance Cost | 340 | 620 | USD | Includes prorated edge-device depreciation |
| Net Annual Benefit | 3,180 | 5,720 | USD | Savings minus maintenance and license |
| Simple Payback Period | 27.9 | 18.5 | months | Matches Table 3 |
| Payback with Demand Response | 21.2 | 14.8 | months | 15-25% additional revenue, not included in main text figures |
| 5-Year ROI | 115% | 224% | % | Matches Table 3 |
| Cost Reduction at 150 buildings | 21.7% | 21.7% | % | Driven primarily by amortization of digital twin engineering effort |

S12. Sensitivity Analysis

| Table S11. Sensitivity Analysis of Key Parameters on Framework Performance |  |  |  |  |
| --- | --- | --- | --- | --- |
| Parameter Varied | Range Tested | Energy Savings Impact | Comfort Compliance Impact | Key Finding |
| Reward Weight ωe(energy) | 0.20 to 0.60 | ±6.2% | ∓4.8% | Optimal at 0.40; higher values degrade comfort |
| Reward Weight ωc(comfort) | 0.15 to 0.55 | ∓5.1% | ±3.5% | Optimal at 0.35; diminishing returns above 0.45 |
| Control Interval | 5 to 30 min | −0% to −11.3% | −0% to −5.2% | 15-minute interval loses approximately 8% savings |
| GNN Neighbor Count (k) | 2 to 10 | ±3.4% | ±0.8% | Saturates at k=5; k=3 loses 2.1% coordination benefit |
| Forecast Lead Time | 1 to 4 hours | ±4.7% | ±1.2% | Optimal at 2-2.5 hours; longer leads waste energy |
| Thermal Mass Uncertainty | ±30% | ∓2.8% | ±1.5% | Robust to moderate calibration errors |
| COP Degradation Model Error | ±20% | ∓3.2% | ±0.6% | Pre-cooling strategy adapts automatically |
| Occupancy Prediction Accuracy | 70% to 95% | ±5.8% | ±3.1% | Current 89% accuracy near optimal tradeoff |
| Electricity Tariff | 0.02 to 0.08 USD/kWh | Linear scaling | No impact | Economic viability scales proportionally |
| Building Network Size | 8 to 150 | +0% to +3.4% | ±0.3% | Coordination benefit saturates beyond 50-75 buildings |
| Dust Storm Frequency | 10 to 40 events/year | ±2.1% | ±1.8% | Framework adapts to varying storm patterns |
| Pre-cooling Temperature Target | 21 to 23°C | ±1.9% | ±2.4% | 22°C optimal for most building types |

S13. Building-Level Savings Distribution and Confidence Intervals

Table S13 reports individual building-level energy savings relative to conventional control, with 95% confidence intervals obtained through building-level bootstrap resampling with 1000 iterations, as referenced in Section 2.10.

| Table S13. Building-Level Energy Savings with 95% Confidence Intervals |  |  |  |
| --- | --- | --- | --- |
| Building ID | Energy Savings (%) | 95% CI Lower | 95% CI Upper |
| RB-01 | 34.2 | 30.1 | 38.3 |
| RB-02 | 33.8 | 29.5 | 38.1 |
| RB-03 | 38.9 | 34.7 | 43.1 |
| RB-04 | 40.1 | 35.8 | 44.4 |
| RB-05 | 35.6 | 31.2 | 40.0 |
| RB-06 | 36.4 | 32.0 | 40.8 |
| CB-01 | 43.5 | 39.0 | 48.0 |
| CB-02 | 40.1 | 35.6 | 44.6 |
| Residential Mean | 36.5 | 33.1 | 39.9 |
| Commercial Mean | 41.8 | 37.4 | 46.2 |
| Portfolio Weighted Mean | 37.8 | 35.9 | 39.7 |

S14. Community-Scale Simulation Methodology

This section documents the procedure used to generate the 150-building synthetic community referenced in Section 2.11 and Section 3.7 of the main text. All results derived from this procedure are simulation-based and were not obtained through additional field deployment.

Building-level parameters for the synthetic community were drawn from probability distributions fitted to the eight calibrated field buildings rather than sampled directly from the field dataset, so as to generate a larger and more varied population while preserving the statistical structure observed on site. Floor area was sampled from a truncated normal distribution fitted separately for residential and commercial archetypes, using the field-observed means and standard deviations reported in Table 1 of the main text, bounded at plus or minus 40% of the observed range to avoid unrealistic outliers. Insulation R-value was sampled from a uniform distribution spanning the field-observed range of 2.0 to 3.8 m²·K/W for residential buildings and 2.0 to 3.5 m²·K/W for commercial buildings, the latter widened slightly beyond the two monitored facilities to reflect plausible regional variation. HVAC coefficient of performance was sampled from a truncated normal distribution centered on the field-observed mean, reproducing the observed range of 2.7 to 3.6. Window-to-wall ratio was assigned using typical regional construction values of 15 to 25% for residential units and 25 to 40% for commercial units, based on regional building code guidance. Construction vintage was sampled uniformly across the 2005 to 2020 range.

The synthetic community preserved a 4:1 ratio of residential to commercial buildings, yielding 120 residential and 30 commercial buildings for the 150-building case, and proportionally scaled populations for the 30, 75, and 150-building steps reported in Table 4 of the main text. The matched homogeneous residential-only community used for comparison in Section 3.7 was generated using the identical procedure restricted to residential parameter distributions, producing a 150-building population with no commercial nodes and a corrected projected saving of 37.9%, as reported in the response to Reviewer 1, Comment 15.

Buildings were placed on a synthetic grid using inter-building spacing values sampled from the range of centroid distances measured across the eight field buildings, reported in Table 8 of the main text, approximately 15 to 85 meters. Graph edges for the synthetic community followed the same four relationship types defined in Section 2.5.1, applied to the larger synthetic node set. The GNN and DRL components were initialized from the weights obtained through field training on the eight-building cluster and further trained on the synthetic environment for 500,000 timesteps prior to evaluation, using the same PPO hyperparameters and reward structure described in Sections 2.6 and 2.7.

This procedure carries forward the calibration accuracy and modeling assumptions established for the eight field buildings but does not independently validate performance for building types, envelope characteristics, or climate microzones outside the range represented in the original field cluster. Practical deployment factors, including communication network reliability across a substantially larger number of edge devices, field commissioning and maintenance workload, and possible degradation in multi-agent coordination as graph size grows, were not modeled and are not reflected in the reported figures.

S15. Monte Carlo Uncertainty Propagation Analysis

Table S15 summarizes the Monte Carlo uncertainty propagation analysis referenced in Section 2.10 of the main text. Ten thousand samples were drawn jointly from the accuracy specifications of the deployed sensors, the occupancy estimation error distribution characterized in Section 2.3, and the posterior parameter distributions obtained from the Bayesian digital twin calibration described in Section 2.4.7, and propagated through the reported energy savings calculation.

| Table S15. Contribution of Uncertainty Sources to Propagated Energy Savings Interval |  |  |
| --- | --- | --- |
| Uncertainty Source | Input Range Sampled | Approximate Contribution to Output Variance (%) |
| Power meter and temperature sensor accuracy | Per Section 2.3 specifications | 18 |
| Occupancy estimation error | ±15% occupancy count, per Section 2.3 validation | 34 |
| Digital twin calibration parameter posterior | Per Section 2.4.7 MCMC posteriors | 48 |
| Combined propagated 90% CI for overall energy savings | — | 35.3% to 40.1% |