Sustainable Municipal Wastewater Treatment Using an Innovative Integrated Compact Unit: Microbial Communities, Parasite Removal, and Techno-Economic Analysis

Mohamed El-Khateeb1, Gamal Hassan1, Mohamed Azab El-Liethy2, Kamel M. El-Khatib3, Hussein Abdel-Shafy1, Anyi Hu4, Mahmoud Gad5*

1Water Pollution Research Department, National Research Centre, Dokki, 12622, Giza, Egypt

2Environmental Microbiology Lab., Water Pollution Research Department, National Research Centre, Dokki, 12622, Giza, Egypt

3Chemical Engineering & Pilot Plant Department, Engineering Research and Renewable Energy Institute, National Research Centre, Dokki, 12622, Giza, Egypt

4 CAS Key Laboratory of Urban Pollutant Conversion, Institute of Urban Environment, Chinese Academy of Sciences, Xiamen 361021, China; ayhu@iue.ac.cn

5Environmental Parasitology Lab., Water Pollution Research Department, National Research Centre, Dokki, 12622, Giza, Egypt

* Correspondence: mi.saleh@nrc.sci.eg or mahmoudafw@yahoo.com; Tel.: +20-106-113-2911

Figure S1. Schematic diagram of the compact unit for 100 persons; 1) two overlapped UASB reactors (anaerobic stage); DHNW reactor (aerobic stage); ABR reactor, and chlorine unit.

Table S1. Operating conditions of the compact unit during one year working (Junrary-December 2022)

| Primary treatment step (UASB) |  |  |
| --- | --- | --- |
| Parameter | Unit | Value |
| Length | m | 1.25 |
| Width | m | 1.0 |
| Height | m | 2.0 |
| Detention time (DT) | Hr | 5.0 |
| Organic loading rate (OLR) | Kg COD/m3/d Kg BOD/ m3/d | 1.8 1.4 |
| Hydraulic loading rate (HLR) | m3/m3/d | 4.8 |
| Secondary treatment step (DHNW) |  |  |
| Parameter | Unit | Value |
| Length | m | 0.75 |
| Width | m | 1.0 |
| Height | m | 2.0 |
| No. of pieces of packing material | No. | 40,000 |
| Detention time (DT) | Hr | 5 |
| Total Surface area of packing material | m2/m3 | 293.3 |
| Hydraulic loading rate (HLR) | m/h | 0.5 |
| Organic loading rate (OLR) | Kg COD/m3.packing material/d Kg BOD/m3.packing material/d | 3.4 2.4 |
| Ammonia loading rate (ALR) | Kg N/m3.packing material/d | 0.7 |
| Hydraulic loading rate (HLR) | m3/m3. packing material/d | 24 |

Figure S2: Process flow sheet of the Anaerobic/aerobic bioreactor compact unit wastewater treatment plant

Figure S3: Layout of the aerobic/anaerobic wastewater treatment compact unit

Figure S4. Alpha diversity measurements of microbial communities in the different treatment stages.