Supplementary material

Additional file 1. Carbon dioxide and particulate matter results by room and nursing home, AIR-CO, 2022

|  | CO2 (PPM) | CO2 (PPM) | CO2 (PPM) | CO2 (PPM) | CO2 (PPM) | PM 2.5 (µg/m3) | PM 2.5 (µg/m3) | PM 2.5 (µg/m3) | PM 2.5 (µg/m3) | PM 2.5 (µg/m3) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Night (9pm-6am) | Morning (6am-11am) | Midday (11am-1pm) | Afternoon (1pm-4pm) | Evening (4pm-9pm) | Night (9pm-6am) | Morning (6am-11am) | Midday (11am-1pm) | Afternoon (1pm-4pm) | Evening (4pm-9pm) |
|  | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) |
| All NHs (n=11) | 576 (1554) | 592 (1622) | 587 (1441) | 574 (1905) | 570 (2159) | 4.1 (157.6) | 4.7 (135.2) | 4.6 (310.6) | 4.4 (22.9) | 4.1 (95.3) |
| NH1 (Ventilation Type A and C) |  |  |  |  |  |  |  |  |  |  |
| Resident room | 645 (1554) | 749 (1622) | 767 (1283) | 637 (951) | 706 (2029) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Common room for residents | 568 (900) | 767 (1340) | 841 (1278) | 791 (1072) | 811 (1082) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Staff room | 563 (914) | 754 (1170) | 772 (1174) | 701 (972) | 741 (1019) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Common room for residents | 548 (740) | 539 (896) | 590 (867) | 556 (758) | 566 (1027) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | 1252 (1520) | 970 (1597) | 639 (831) | 611 (915) | 818 (1314) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| NH2 (Ventilation Type A) |  |  |  |  |  |  |  |  |  |  |
| Entrance hall/cafeteria | 467 (531) | 542 (826) | 567 (805) | 589 (789) | 502 (675) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Common room for residents | 535 (764) | 659 (1169) | 767 (1168) | 775 (1231) | 721 (1110) | 5.6 (7.8) | 5.9 (10.7) | 6.0 (11.2) | 5.7 (7.5) | 5.7 (19.8) |
| Resident room | 961 (1247) | 778 (1124) | 569 (791) | 741 (1905) | 826 (2159) | 4.9 (9.0) | 5.6 (29.3) | 5.6 (8.3) | 5.1 (7.5) | 4.7 (7.0) |
| Resident room | 1028 (1186) | 935 (1320) | 745 (1024) | 742 (1433) | 937 (1489) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Staff room | 500 (565) | 553 (832) | 529 (975) | 535 (819) | 488 (625) | 5.5 (9.8) | 5.7 (10.4) | 6.0 (11.2) | 6.1 (16.4) | 5.7 (9.1) |
| NH3 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Staff room | 441 (511) | 467 (674) | 555 (948) | 550 (1199) | 454 (795) | 4.4 (25.8) | 4.7 (46.0) | 4.1 (7.5) | 4.2 (13.4) | 4.5 (28.7) |
| Common room for residents | 463 (516) | 526 (635) | 592 (732) | 514 (637) | 497 (656) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | 732 (908) | 594 (814) | 518 (596) | 565 (791) | 581 (712) | 3.4 (6.1) | 4.4 (72.5) | 3.9 (11.3) | 3.1 (5.8) | 2.8 (4.1) |
| Entrance hall/cafeteria | 450 (524) | 467 (543) | 477 (547) | 526 (689) | 470 (735) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | 635 (888) | 586 (882) | 526 (623) | 526 (650) | 538 (668) | 4.4 (10.0) | 5.0 (135.2) | 4.3 (7.7) | 4.5 (7.2) | 4.2 (8.2) |
| NH4 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Resident room | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | 926 (1207) | 766 (943) | 595 (844) | 677 (1018) | 843 (1039) | 3.2 (5.3) | 3.9 (9.4) | 4.2 (8.0) | 3.7 (7.9) | 3.3 (4.7) |
| Staff room | 427 (485) | 492 (785) | 568 (1178) | 512 (697) | 450 (542) | 4.5 (17.9) | 3.9 (15.2) | 3.9 (10.1) | 3.8 (7.6) | 3.9 (37.2) |
| Common room for residents | 510 (620) | 530 (648) | 504 (711) | 503 (718) | 502 (735) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Other | 507 (643) | 616 (1346) | 656 (1441) | 589 (856) | 551 (688) | 3.0 (3.7) | 3.7 (8.6) | 4.1 (7.0) | 4.0 (7.3) | 3.3 (4.9) |
| NH5 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Entrance hall/cafeteria | 483 (619) | 520 (648) | 530 (616) | 516 (633) | 516 (667) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | 543 (661) | 590 (903) | 591 (789) | 617 (881) | 591 (759) | 4.1 (6.2) | 4.2 (22.8) | 4.1 (7.4) | 3.8 (6.2) | 4.1 (11.0) |
| Resident room | 621 (1061) | 604 (706) | 583 (720) | 591 (714) | 620 (861) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Common room for residents | 501 (603) | 526 (614) | 666 (983) | 560 (849) | 504 (657) | 3.6 (6.2) | 3.6 (9.3) | 4.1 (7.0) | 3.8 (6.8) | 3.0 (4.1) |
| Staff room | 468 (567) | 507 (660) | 620 (886) | 550 (872) | 495 (844) | 3.6 (6.5) | 3.8 (10.0) | 4.7 (8.2) | 4.3 (9.8) | 3.6 (5.2) |
| NH6 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Entrance hall/cafeteria | 514 (664) | 558 (853) | 618 (854) | 566 (1043) | 503 (643) | 4.5 (6.6) | 5.1 (10.1) | 5.3 (7.4) | 5.1 (8.9) | 4.1 (5.7) |
| Staff room | 505 (605) | 496 (598) | 505 (798) | 595 (887) | 547 (952) | 4.6 (17.3) | 3.8 (9.9) | 3.8 (6.6) | 3.8 (22.9) | 3.8 (37.2) |
| Resident room | 770 (902) | 652 (873) | 584 (731) | 587 (690) | 610 (794) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Common room for residents | 511 (630) | 607 (916) | 673 (979) | 597 (813) | 583 (928) | 3.6 (6.8) | 3.7 (8.4) | 3.7 (5.8) | 3.7 (11.1) | 3.5 (4.7) |
| Resident room | 745 (904) | 607 (752) | 599 (754) | 622 (777) | 599 (805) | 3.2 (4.6) | 3.7 (8.1) | 3.4 (5.8) | 3.1 (5.1) | 3.3 (5.5) |
| NH7 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Common room for residents | 554 (709) | 657 (948) | 710 (976) | 551 (785) | 602 (943) | 6.0 (8.7) | 6.9 (11.1) | 7.6 (10.4) | 6.7 (8.3) | 6.0 (7.9) |
| Staff room | 521 (626) | 566 (736) | 535 (727) | 574 (836) | 504 (688) | 6.0 (11.3) | 6.9 (10.3) | 8.5 (12.1) | 10.0 (18.0) | 6.7 (11.6) |
| Resident room | 604 (774) | 650 (847) | 628 (805) | 591 (851) | 635 (994) | 9.8 (157.6) | 7.22 (11.7) | 7.5 (11.0) | 6.5 (9.7) | 5. 7 (10.1) |
| Entrance hall/cafeteria | 537 (669) | 572 (697) | 532 (614) | 597 (1010) | 570 (1008) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | 574 (800) | 589 (1086) | 494 (599) | 502 (883) | 510 (742) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| NH8 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Resident room | 507 (632) | 578 (973) | 582 (782) | 571 (795) | 534 (731) | 2.9 (8.7) | 10.4 (130.6) | 3.1 (6.7) | 3.0 (5.3) | 7.6 (95.3) |
| Common room for residents | 462 (530) | 544 (725) | 617 (812) | 547 (747) | 515 (756) | 2.1 (3.3) | 3.0 (6.5) | 2.5 (8.5) | 2.2 (4.4) | 2.4 (17.3) |
| Common room for residents | 411 (480) | 467 (592) | 494 (582) | 490 (595) | 438 (613) | 3.0 (6.4) | 3.7 (10.9) | 3.8 (9.8) | 3. 6 (7.1) | 3.4 (11.3) |
| Staff room | 466 (538) | 470 (726) | 476 (730) | 458 (552) | 453 (496) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | 633 (829) | 681 (1065) | 589 (762) | 594 (798) | 610 (782) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| NH9 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Common room for residents | 500 (557) | 536 (711) | 569 (747) | 553 (714) | 511 (744) | 3.5 (12.3) | 2.8 (15.4) | 2.9 (8.0) | 3.0 (8.5) | 2.8 (8.2) |
| Resident room | 507 (648) | 540 (710) | 508 (620) | 506 (615) | 510 (633) | 3.3 (7.1) | 3.8 (13.6) | 3.7 (7.6) | 4.2 (14.8) | 3.3 (8.4) |
| Staff room | 462 (560) | 483 (618) | 497 (646) | 461 (687) | 452 (544) | 3.1 (10.6) | 4.3 (10.3) | 4.0 (9.5) | 4.4 (18.6) | 3.7 (11.6) |
| Entrance hall/cafeteria | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | 4.1 (5.3) | 5.1 (10.1) | 4.8 (8.2) | 5.4 (13.1) | 4.3 (10.8) |
| Common room for residents | 451 (505) | 522 (1082) | 542 (775) | 520 (625) | 484 (627) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| NH10 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Other | 436 (516) | 461 (680) | 454 (564) | 430 (489) | 420 (491) | 2.7 (3.5) | 3.3 (117.1) | 6.9 (310.6) | 3.0 (4.4) | 2.6 (3.7) |
| Resident room | 532 (676) | 590 (806) | 621 (763) | 598 (693) | 590 (772) | 2.8 (3.7) | 3.0 (5.2) | 3.4 (6.7) | 3.1 (5.1) | 3.1 (4.6) |
| Common room for residents | 489 (616) | 553 (856) | 541 (648) | 516 (651) | 514 (653) | 4.2 (5.2) | 4.8 (31.0) | 5.4 (12.3) | 5.9 (14.1) | 5.2 (39.9) |
| Staff room | 459 (563) | 455 (575) | 439 (486) | 470 (1043) | 475 (686) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| NH11 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Common room for residents | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Staff room | 424 (488) | 435 (484) | 517 (743) | 533 (683) | 472 (703) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Entrance hall/cafeteria | 488 (603) | 515 (675) | 541 (803) | 516 (627) | 508 (699) | 4.5 (8.5) | 4.1 (11.0) | 3.8 (6.8) | 4.2 (7.6) | 4.1 (10.9) |
| Resident room | 796 (1101) | 665 (1151) | 586 (791) | 568 (842) | 607 (938) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | 723 (1040) | 700 (1063) | 699 (860) | 667 (1020) | 592 (804) | 3.8 (5.8) | 5.0 (98.0) | 4.3 (11.6) | 3.8 (10.1) | 3.7 (7.0) |

NH: nursing home; CO2: carbon dioxide; PM: particulate matter; PM 2.5: particles with an aerodynamic diameter of 2.5 micrometer (µm) or less; Ventilation Type A:   natural ventilation; Ventilation Type C: Natural supply with mechanical exhaust; Ventilation Type D: Fully mechanical ventilation

| Legend |  |  |  |
| --- | --- | --- | --- |
| CO2 |  | PM (WHO annual mean) |  |
| Average mean | 900-1200 | Too high mean | >5 µg/m³ |
| Too high mean | >1200 | Too high maximum | >5 µg/m³ |
| Average maximum | 900-1200 |  |  |
| Too high maximum | >1200 |  |  |