Supplementary material

Additional file 2. Indoor temperature and relative humidity results by room and nursing home, AIR-CO, 2022

|  | Temp (°C) | Temp (°C) | Temp (°C) | Temp (°C) | Temp (°C) | RH (%) | RH (%) | RH (%) | RH (%) | RH (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Night (9pm-6am) | Morning (6am-11am) | Midday (11am-1pm) | Afternoon (1pm-4pm) | Evening (4pm-9pm) | Night (9pm-6am) | Morning (6am-11am) | Midday (11am-1pm) | Afternoon (1pm-4pm) | Evening (4pm-9pm) |
|  | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) | Mean (max) |
| All NHs (n=11) | 23.9 (12.0-30.2) | 24.0 (14.3-32.4) | 24.6 (16.0-30) | 24.7 (15.5-29.5) | 24.6 (15.6-33.7) | 29.1 (56.5) | 28.8 (57.0) | 29.1 (61.9) | 28.7 (50.8) | 28.5 (56.2) |
| NH1 (Ventilation Type A and C) |  |  |  |  |  |  |  |  |  |  |
| Resident room | 21.7 (23.8) | 22.2 (27.9) | 23.6 (24.9) | 22.4 (24.1) | 22.3 (24.3) | 32.9 (43.1) | 33.4 (49.9) | 33.6 (49.8) | 33.4 (43.7) | 34.2 (46.7) |
| Common room for residents | 22.5 (23.7) | 23.4 (27.1) | 26.2 (27.6) | 24.4 (26.4) | 24.4 (26.5) | 34.6 (49.2) | 32.0 (43.0) | 30.1 (43.1) | 31.6 (42.0) | 31.2 (41.2) |
| Staff room | 21.3 (23.5) | 20.8 (23.3) | 22.6 (24.0) | 22.6 (23.8) | 22.7 (24.4) | 36.6 (56.5) | 36.8 (46.4) | 38.0 (52.8) | 35.9 (46.7) | 35.9 (56.2) |
| Common room for residents | 22.8 (23.6) | 23.0 (24.0) | 23.7 (24.6) | 23.8 (27.0) | 23.2 (24.5) | 22.8 (23.6) | 23.0 (24.0) | 23.7 (24.6) | 23.8 (27.0) | 23.2 (24.5) |
| Resident room | 20.4 (21.9) | 20.8 (23.4) | 21.0 (22.5) | 20.6 (21.4) | 21.1 (22.3) | 20.4 (21.9) | 20.8 (23.4) | 21.0 (22.5) | 20.6 (21.4) | 21.1 (22.3) |
| NH2 (Ventilation Type A) |  |  |  |  |  |  |  |  |  |  |
| Entrance hall/cafeteria | 17.6 (19.2) | 19.5 (21.1) | 20.9 (21.6) | 21.2 (21.9) | 20.2 (21.6) | 31.4 (38.7) | 30.0 (38.7) | 29.6 (33.0) | 29.6 (33.1) | 29.3 (35.4) |
| Common room for residents | 22.9 (24.2) | 22.9 (24.9) | 23.9 (25.2) | 23.9 (25.4) | 23.8 (25.0) | 23.9 (27.4) | 24.4 (30.4) | 25.7 (31.4) | 25.8 (30.8) | 25.4 (29.4) |
| Resident room | 24.5 (25.2) | 24.0 (25.3) | 24.2 (25.5) | 24.6 (25.5) | 24.6 (25.5) | 25.6 (30.5) | 25.2 (30.4) | 23.9 (28.7) | 24.2 (29.3) | 24.5 (29.6) |
| Resident room | 23.4 (24.9) | 23.0 (24.9) | 24.2 (25.1) | 24.3 (25.1) | 24.4 (24.9) | 30.9 (34.3) | 31.2 (36.4) | 28.2 (31.8) | 27.4 (34.0) | 27.9 (34.2) |
| Staff room | 17.9 (19.2) | 18.1 (19.8) | 18.5 (19.7) | 18.2 (19.3) | 18.1 (19.2) | 29.0 (33.5) | 28.9 (34.5) | 29.0 (58.4) | 28.9 (36.1) | 28.7 (34.8) |
| NH3 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Staff room | 22.8 (23.4) | 22.6 (23.3) | 23.4 (24.0) | 23.9 (25.0) | 23.4 (24.9) | 25.0 (35.4) | 24.7 (36.7) | 25.7 (32.0) | 25.6 (30.3) | 24.9 (31.6) |
| Common room for residents | 24.0 (25.7) | 24.7 (27.8) | 26.1 (27.4) | 25.6 (26.7) | 25.3 (26.6) | 26.1 (33.6) | 25.9 (34.4) | 26.6 (33.6) | 27.5 (33.0) | 26.7 (33.0) |
| Resident room | 28.8 (29.3) | 28.4 (30.5) | 28.3 (29.0) | 28.5 (28.8) | 28.4 (29.2) | 21.9 (29.8) | 20.7 (32.9) | 21.2 (27.5) | 21.4 (27.7) | 21.5 (27.8) |
| Entrance hall/cafeteria | 24.4 (24.9) | 24.1 (24.7) | 24.2 (25.0) | 24.4 (25.2) | 24.4 (25.2) | 22.6 (31.0) | 22.5 (33.2) | 22.8 (28.6) | 22.9 (28.7) | 22.5 (29.0) |
| Resident room | 28.1 (29.4) | 27.6 (29.0) | 27.6 (29.4) | 27.8 (29.5) | 28.2 (29.3) | 28.3 (35.6) | 28.2 (43.6) | 28.8 (36.5) | 28.6 (33.9) | 28.3 (38.0) |
| NH4 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Resident room | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | 25.9 (27.1) | 25.5 (26.8) | 25.7 (26.8) | 26.4 (27.4) | 26.8 (28.1) | 25.7 (32.8) | 24.9 (33.2) | 24.6 (34.9) | 24.0 (29.9) | 25.0 (31.1) |
| Staff room | 26.6 (27.1) | 26.4 (27.1) | 26.2 (27.0) | 26.2 (27.0) | 26.4 (27.0) | 22.9 (29.8) | 23.2 (29.9) | 24.6 (30.6) | 25.5 (32.3) | 23.9 (28.6) |
| Common room for residents | 20.3 (23.7) | 22.2 (25.2) | 24.3 (25.6) | 25.3 (28.2) | 23.4 (32.0) | 30.2 (41.4) | 28.6 (40.9) | 25.9 (32.4) | 25.6 (31.3) | 27.5 (39.5) |
| Other | 24.2 (24.4) | 24.5 (25.1) | 24.6 (25.0) | 24.6 (25.1) | 24.4 (25.0) | 26.7 (32.2) | 26.6 (32.9) | 27.3 (39.0) | 27.9 (38.1) | 27.4 (34.1) |
| NH5 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Entrance hall/cafeteria | 22.8 (24.3) | 22.1 (23.7) | 22.9 (23.8) | 23.6 (27.1) | 23.5 (33.7) | 29.7 (44.5) | 31.0 (37.9) | 31.0 (43.6) | 29.2 (41.9) | 28.4 (41.9) |
| Resident room | 24.5 (27.7) | 24.4 (27.4) | 24.4 (27.1) | 24.5 (26.6) | 24.5 (27.7) | 29.0 (38.5) | 29.7 (36.3) | 31.0 (36.5) | 29.9 (35.9) | 28.8 (36.6) |
| Resident room | 27.1 (30.2) | 25.6 (28.9) | 26.2 (27.5) | 26.4 (28.0) | 26.5 (29.8) | 26.0 (36.2) | 27.7 (36.1) | 27.9 (33.6) | 26.9 (34.1) | 26.7 (35.4) |
| Common room for residents | 23.1 (24.6) | 23.2 (24.6) | 24.2 (25.7) | 24.3 (25.7) | 23.9 (25.3) | 28.6 (41.5) | 28.5 (36.5) | 31.2 (61.9) | 30.0 (44.2) | 27.0 (37.8) |
| Staff room | 24.3 (25.9) | 24.6 (25.9) | 24.9 (26.2) | 24.8 (26.0) | 24.6 (26.1) | 27.8 (42.2) | 27.8 (35.1) | 30.4 (39.0) | 29.9 (41.1) | 27.3 (39.0) |
| NH6 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Entrance hall/cafeteria | 23.6 (24.7) | 23.5 (24.5) | 23.7 (24.5) | 23.6 (24.4) | 23.7 (24.7) | 31.4 (40.9) | 31.9 (42.2) | 35.2 (50.5) | 33.3 (43.5) | 31.5 (40.5) |
| Staff room | 25.5 (26.4) | 24.7 (25.2) | 25.1 (25.5) | 25.9 (27.5) | 26.2 (27.5) | 27.7 (37.2) | 28.9 (40.2) | 28.8 (35.7) | 28.6 (37.4) | 27.2 (37.9) |
| Resident room | 25.6 (27.4) | 25.1 (26.0) | 25.6 (26.4) | 25.7 (26.5) | 25.9 (27.3) | 30.5 (39.1) | 30.6 (40.9) | 30.0 (37.0) | 29.2 (37.5) | 28.4 (37.4) |
| Common room for residents | 25.0 (25.6) | 24.6 (25.3) | 25.2 (26.2) | 25.5 (26.8) | 25.3 (26.0) | 27.6 (38.4) | 29.2 (42.0) | 31.5 (42.1) | 29.4 (45.4) | 27.7 (40.8) |
| Resident room | 24.1 (25.2) | 23.6 (25.1) | 24.7 (25.4) | 25.2 (26.1) | 24.7 (26.2) | 24.1 (25.2) | 23.6 (25.1) | 24.7 (25.4) | 25.2 (26.1) | 24.7 (26.2) |
| NH7 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Common room for residents | 24.3 (25.0) | 24.6 (25.6) | 25.0 (25.8) | 25.1 (25.6) | 25.1 (25.7) | 29.4 (38.1) | 30.0 (38.2) | 31.2 (42.2) | 28.4 (41.8) | 28.7 (40.2) |
| Staff room | 23.5 (24.9) | 24.5 (25.1) | 23.9 (24.4) | 23.8 (24.3) | 23.7 (24.2) | 30.8 (37.5) | 29.6 (37.4) | 31.8 (38.6) | 34.9 (45.6) | 32.3 (42.6) |
| Resident room | 25.8 (26.4) | 25.5 (26.0) | 26.0 (26.3) | 26.1 (26.3) | 26.1 (26.3) | 28.6 (36.2) | 28.8 (35.9) | 29.7 (35.6) | 27.9 (36.8) | 28.4 (37.5) |
| Entrance hall/cafeteria | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Resident room | 25.4 (26.5) | 25.5 (26.2) | 25.7 (26.5) | 25.6 (26.2) | 25.6 (26.4) | 27.8 (36.7) | 28.5 (39.0) | 28.0 (36.3) | 26.9 (36.5) | 26.6 (37.5) |
| NH8 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Resident room | 24.1 (26.1) | 23.7 (25.8) | 24.4 (25.5) | 24.7 (25.9) | 24.8 (26.1) | 26.7 (34.1) | 27.0 (40.0) | 26.3 (35.8) | 24.9 (34.7) | 25.8 (34.1) |
| Common room for residents | 24.0 (26.4) | 23.9 (26.4) | 24.4 (25.8) | 24.1 (25.6) | 23.9 (25.2) | 26.9 (36.1) | 27.0 (34.9) | 27.2 (35.1) | 25.5 (33.7) | 27.4 (41.7) |
| Common room for residents | 24.3 (25.9) | 25.0 (26.3) | 25.4 (26.5) | 25.7 (26.8) | 25.6 (27.1) | 25.8 (35.2) | 24.6 (34.9) | 24.2 (34.4) | 23.1 (32.7) | 24.5 (33.7) |
| Staff room | 19.8 (21.6) | 19.7 (22.0) | 20.1 (22.2) | 20.0 (22.0) | 20.0 (21.7) | 31.4 (39.2) | 30.1 (44.9) | 29.2 (41.8) | 28.2 (38.7) | 30.5 (39.2) |
| Resident room | 24.3 (25.5) | 24.5 (25.2) | 24.7 (25.2) | 24.7 (25.4) | 24.7 (25.6) | 28.2 (34.6) | 28.4 (47.7) | 26.9 (37.9) | 25.5 (33.7) | 26.8 (34.3) |
| NH9 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Common room for residents | 23.0 (24.7) | 23.9 (25.0) | 24.6 (25.3) | 24.7 (25.3) | 24.3 (25.8) | 24.6 (37.6) | 24.1 (35.5) | 24.0 (38.2) | 23.0 (36.0) | 24.0 (34.4) |
| Resident room | 25.7 (27.7) | 25.9 (27.8) | 25.7 (26.7) | 25.5 (27.2) | 25.8 (27.6) | 22.9 (30.6) | 23.5 (35.7) | 23.0 (33.6) | 22.7 (33.1) | 23.5 (31.7) |
| Staff room | 22.8 (24.4) | 22.6 (24.8) | 23.8 (25.0) | 23.8 (24.6) | 23.4 (24.8) | 27.6 (36.5) | 28.2 (40.9) | 27.0 (41.4) | 26.0 (38.8) | 27.7 (36.4) |
| Entrance hall/cafeteria | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Common room for residents | 25.2 (26.3) | 25.5 (26.8) | 26.0 (27.0) | 26.0 (26.6) | 26.0 (26.7) | 23.4 (34.2) | 24.4 (44.0) | 24.2 (37.8) | 23.2 (34.7) | 23.8 (35.2) |
| NH10 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Other | 23.4 (24.2) | 23.5 (25.6) | 23.9 (25.6) | 24.0 (24.7) | 24.1 (24.6) | 37.1 (43.8) | 36.5 (52.3) | 36.9 (52.5) | 36.7 (45.3) | 37.0 (43.3) |
| Resident room | 26.0 (27.0) | 25.5 (26.3) | 26.0 (26.5) | 26.3 (26.9) | 26.5 (27.1) | 34.6 (39.4) | 34.2 (43.5) | 35.7 (43.8) | 36.0 (41.9) | 35.6 (41.5) |
| Common room for residents | 26.9 (28.8) | 27.1 (32.4) | 28.0 (30.0) | 28.3 (29.4) | 28.3 (29.7) | 32.6 (37.1) | 32.7 (50.2) | 32.9 (47.4) | 33.3 (47.9) | 33.2 (45.1) |
| Staff room | 21.5 (22.8) | 22.0 (23.6) | 23.2 (23.8) | 22.6 (23.7) | 22.5 (23.2) | 41.6 (47.3) | 40.1 (57.0) | 38.6 (48.7) | 41.5 (50.8) | 42.5 (52.0) |
| Resident room | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| NH11 (Ventilation Type D) |  |  |  |  |  |  |  |  |  |  |
| Common room for residents | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) | NA (NA) |
| Staff room | 26.2 (28.3) | 26.4 (28.0) | 26.8 (28.0) | 26.1 (26.8) | 26.9 (29.5) | 35.2 (40.2) | 34.9 (44.1) | 39.5 (49.4) | 37.3 (43.7) | 35.5 (42.0) |
| Entrance hall/cafeteria | 25.3 (26.9) | 25.7 (26.8) | 26.8 (27.6) | 26.6 (27.3) | 26.6 (27.4) | 34.9 (40.3) | 33.2 (42.6) | 33.1 (40.7) | 33.8 (41.5) | 34.0 (41.1) |
| Resident room | 23.3 (25.3) | 24.1 (26.9) | 24.7 (26.4) | 25.6 (27.2) | 25.5 (26.9) | 43.8 (49.4) | 39.4 (49.1) | 37.9 (47.2) | 36.4 (44.4) | 37.4 (45.9) |
| Resident room | 25.0 (27.4) | 25.7 (26.8) | 26.5 (27.5) | 26.9 (27.7) | 27.2 (29.0) | 39.9 (47.2) | 37.2 (46.2) | 36.9 (44.5) | 36.1 (42.4) | 35.1 (40.5) |

NH: nursing home; Temp: temperature; RH: relative humidity; Ventilation Type A:   natural ventilation; Ventilation Type C: Natural supply with mechanical exhaust; Ventilation Type D: Fully mechanical ventilation

| Legend |  |  |  |
| --- | --- | --- | --- |
| Temperature |  | RH |  |
| Too low mean | <22°C | Too low mean | < 40% |
| Too high mean | >26°C | Too high mean | > 60% |
| Too low maximum | <22°C | Too low maximum | < 40% |
| Too high maximum | >26°C | Too high maximum | > 60% |